Primary Sedimentation tank

Purpose:

1- Removal of 40 - 60 % of suspended solids 
2- Removal of 25 - 35 % of B.O.D.  
3- Sediment the organic and inorganic matters to improve the properties of the sewage and prepare it for the biological treatment.

Types of primary sedimentation tanks:

1- Rectangular tank.

2- Circular tank.

Factors affecting sedimentation efficiency:

1- Viscosity 
2- Concentration of suspended solids 
3- Retention period 
4- Horizontal velocity 
5- Temperature 
6- Surface loading rate = 24 - 48 m³/m²/day

Primary sedimentation tank

(horizontal flow)

Effluent weir of rectangular sedimentation tank

Rectangular primary sedimentation tank

Primary sedimentation tank

(Radial flow)

Circular primary sedimentation tank

7- Dimension of tank 
8- Dead zones.

Design criteria: 
1- Retention period = T = 2 - 3 hrs 
2- Surface loading rate (S.L.R.)  = 24 - 48 m³/m²/day 
3- Horizontal velocity ≤ 0.3 m/min 
4- Effluent weir loading (E.W.L.) ≤ 600 m³/m/day    (≤ 25 m³/m/hr) 
5- L = 3 – 5 B

L ≤ 40 m 
6- d = 3 - 5 m 
7- B = 2 – 3 d

8- Φ ≤ 40 m
9- Bottom slope for circular tank = 4 - 10 %

for rectangular tank = 1 - 2 %

V = Qd x T

S.L.R = Qd / S.A

Example:

For a sewage treatment plant, the following data are given:

- Qave summer = 18000 m3/d

- S.L.R = 30 m3/m2/d

It is required to design primary sedimentation tanks.

Solution:

Qd = 1.5 x 18000 = 27000 m3/d

For rectangular tank:

Assume T = 2.5 hr

≤L/7

≤L/7

Circular primary sedimentation tank:

Example:

Estimate the volume of sludge produced per 27000 m3/d if the influent S.S 300 mg/l. The removal efficiency is 60%.

Solution:

For circular tank: