# iMPACT OF TOWER STAGGERING ON MAGNETIC FIELD

# DISTRIBUTIONs UNDER PARALLEL POWER LINES

### Shaher A. Mahmoud*	        A. H. Hamza**

#### Nagat M. K. Abdel-Gawad**	     Khaled G. Ahmed*

* Egyptian Electricity Holding Company, Cairo, Egypt

** Faculty of Engineering at Shoubra, Cairo, Egypt

Abstract

The impact of tower staggering on the magnetic field distributions under parallel power lines is thoroughly investigated. The staggering techniques are classified into two types; artificial staggering applied at parallel lines with the same span length and natural staggering resulted from parallel lines with different span lengths. The lateral magnetic field profiles of typical parallel lines for both types of staggering are developed and analyzed taken into consideration the effects of staggering distance, one line disconnection, line spacing, phase arrangement, current direction and line loading.

1. Introduction

The interaction between the power frequency magnetic fields and the living organisms still draw worldwide attention because of the results of a number of studies which indicated possible harmful effects due to the exposure to these fields. In parallel to the laboratory and the epidemiological studies, many researches addressed the evaluation of the magnetically-induced currents in living organisms [1,2].

Many studies have been carried out to evaluate the magnetic fields beneath different power lines which are considered as major sources of induction [3-6].  However, these lines are dealt with individually, i.e. magnetic fields are evaluated under single power lines. A recent study was published which investigated the magnetic field distributions under parallel transmission lines [7]. The results showed that the magnetic field profiles under parallel lines were apparently different when compared to those under single lines.

As a matter of fact, in the normal erection of parallel lines’ towers with the same voltage level and configuration (and consequently with the same line span), the towers of the first line are positioned to face the towers of the second line. On the contrary, the erection of parallel power lines’ towers with different voltage levels and configurations (and consequently with different line spans) would result in the displacement (or staggering) of the parallel lines’ towers.

Accordingly, this paper considers the issue of tower staggering impact on the magnetic field distributions under parallel lines using a three-dimensional magnetic field computational technique [8]. Typical 220, 66 and 11 kV power line configurations in Egypt are used for the current study. The magnetic field distributions under parallel 220 kV lines are studied taking into account the proposed artificial staggering technique (i.e. impose staggering on towers of one of the parallel lines). As “naturally staggered” lines, the magnetic field distributions under parallel 220 & 66 kV lines and parallel 66 & 11 kV lines are also evaluated. A comparative study between the considered cases is also carried out taking into account the relative configurations, line loading and phase arrangement as well as the spacing between the parallel lines.

2. Employed power line conductor Configurations

Figures 1a, 1b and 1c present the line conductor configurations and dimensions of the employed 220, 66 and 11 kV lines, respectively. The 220 kV line is with a double circuit tower, a line span of 360 m, two subconductors per phase, a spacing between subconductors of 30 cm and a minimum clearance–to-ground of 7 m.  The 66 kV line is with a double circuit tower, a line span of 250 m, one conductor per phase and a minimum clearance-to-ground of 6 m. On the other hand, the 11 kV line is with a single circuit tower, a line span of 80 m, one conductor per phase and a minimum clearance-to-ground of 6 m.

3. ARTIFICIAL STAGGERING – aPPLICATION AT Parallel 220 kV Lines

Each of the parallel 220 kV lines has the same configuration of Figure 1a with a full load current per phase of 1200 Ampere. The permissible minimum spacing between the nearest conductors of the parallel lines is 14 m, according to the Egyptian standards.

3.1 Magnetic Fields in Case of Normally Erected Towers

In case of erecting parallel transmission lines’ towers with the same voltage level and configuration (and consequently with the same line span), the towers of the first line are normally placed to face the towers of the second line.

Figure 2 shows the lateral magnetic field profiles at tower of parallel 220 kV lines in case of normal erection of towers. It is noticed that two peaks exist near the outermost conductors of the lines. Higher magnetic field values are noticed at distances far from the line when compared to the case of a single line.

On the other hand, and for the same case of normal erection of towers, Figure 3 shows the lateral magnetic field profiles at mid span of parallel 220 kV lines. It is noticed that four peaks exist; two within the spacing between the two lines and other two with higher values near the outermost conductors of the lines. Also, higher magnetic field values are noticed at distances far from the line when compared to the case of a single line.

3.2 Effect of Artificial Staggering

Unlike the case of normal erection of line towers, and as sensitivity analysis, it is supposed that the towers of the second line are staggered (or displaced) from the towers of the first line by a distance which is called “staggering distance”, as simulated in Figure 4.

To investigate such effect on the magnetic fields beneath the parallel lines, Figure 5 shows the lateral magnetic field profile at tower of unstaggered line (line 1) in case of staggering distance equals to half span  (180 m) compared to the lateral profiles in case of normally erected towers. It is noticed that higher magnetic field values are found underneath the staggered line conductors (line 2) located at mid span in this case. When compared to the case of normally erected line towers, the impact on the magnetic field levels underneath the first line  (line 1) is limited.

On the other hand, Figure 6 shows the lateral magnetic field profile at tower of unstaggered line (line 1) in case of staggering distance equals to quarter span    (90 m) compared to the lateral profiles in case of normally erected towers. It is noticed that higher magnetic field values are found underneath the staggered line conductors (line 2). Unlike the above case of a staggering distance equals 180 m, the staggering distance of 90 m would result in reducing the maximum magnetic field underneath the staggered line conductors (line 2) by about 27 %.

4. Natural staggering

Unlike the above case which considered parallel lines of the same voltage level, this case considers parallel lines with different voltage levels; 220 & 66 kV lines and 66 & 11 kV lines. Since these parallel lines have different line spans, their towers are naturally staggered.

4.1 Magnetic Fields Under Parallel 220 & 66 kV Lines

# 4.1.1 Simulation of Parallel 220 & 66 kV Lines

The parallel 220 and 66 kV lines are considered. The 220 kV line has the same configuration of Figure 1a with a full load current per phase of 1200 Ampere, while the 66 kV line has the same configuration, as shown in Figure 1b, with a full load current per phase of 600 Ampere. The permissible minimum spacing between the nearest outer conductors of the parallel lines is 14 m, according to the Egyptian standards.

Figure 7 shows the vertical and horizontal projections of the parallel 220 and 66 kV lines. It is noticed that the first tower of the 66 kV line is placed to face the first tower of the 220 kV line. The two lines are with different line spans, where the 220 kV line has a line span of 360 m while the 66 kV line has a line span of 250 m. Accordingly, a natural line tower staggering occurs with a staggering distance of 110 m multiplier.

4.1.2 Effect of One Line Disconnection

Figure 8 shows the lateral magnetic field profiles at tower of parallel 220 and 66 kV lines taking into account the cases of disconnecting either the 220 kV line or the 66 kV line. It is noticed that the operation of the two lines would result in reducing the maximum magnetic field value as well as the values beneath the adjacent circuits of the lines when compared to the case of single 220 kV line. This can be attributed to the cancellation of magnetic fields among the adjacent innermost conductors. In this case also, higher magnetic field values are found beneath and outside the 66 kV line when compared to the case of single 66 kV line.

4.1.3 Effect of Line Spacing

Figure 9 shows the lateral magnetic field profiles at mid span 3 of 220 kV line for parallel 220 and 66 kV lines for different line spacings; minimum spacing of 14 m and double spacing of 28 m. It is noticed that as the two lines become nearer to each other, the maximum value of magnetic field in the two lines corridor decreases. On the other hand, the maximum value of magnetic field beneath the 66 kV line increases and its location is shifted towards the higher voltage line.

4.1.4 Effect of Line Loading

To consider the variation of load (or current) values between the two parallel lines, Figure 10 shows the comparative magnetic field profiles at mid span 3 of 220 kV line for parallel 220 and 66 kV lines for different line loading. It is noticed that reducing the current of the 220 kV line from its full load to half load value (i.e. both lines are with the same current, 600 Ampere) causes a magnetic field reduction at all locations especially under the 220 kV line. The maximum magnetic field value is reduced by almost the same ratio (one half in this case).

4.2 Magnetic Fields Under Parallel 66 & 11 kV Lines

Another case of parallel lines with different voltage levels is the parallel 66 and 11 kV lines. As previously shown, the 66 kV line has the same configuration of Figure 1b with a full load current per phase of 600 Ampere, while the 11 kV line has the same configuration, as shown in Figure 1c with a full load current per phase of 200 Ampere. The permissible minimum spacing between the nearest outer conductors of the parallel lines is 10 m, according to the Egyptian standards.

4.2.1 Effect of One Line Disconnection

Figure 11 shows the lateral magnetic field profiles at tower of parallel 66 and 11 kV lines taking into account the cases of disconnecting either the 66 kV line or the 11 kV line. It is noticed that the operation of the two lines would result in slightly reducing the maximum magnetic field value as well as the values in the zone of the two lines corridor when compared to the case of single 66 kV line. While remarkable reduction of the magnetic field occurs beneath the 11 kV line when compared to the case of single 11 kV line. In general, the effect of 11 kV line on the resultant magnetic field of parallel 66 and 11 kV lines is very limited.

4.2.2 Effect of Phase Arrangement

Figure 12 shows the effect of phase arrangement on the magnetic field distribution under the parallel 66 and 11 kV lines. The 11 kV line as well as the farthest circuit of the 66 kV line are estimated to have a normal phase arrangement (abc) while the adjacent circuit of the 66 kV line is estimated to have a varying phase arrangement. Three different phase arrangements are, thus, considered; (abc, abc/abc), (abc, bca/abc) and (abc, cab/abc). It is noticed that the normal phase arrangement (abc, abc/abc) produces the lowest maximum magnetic field value while produces the highest magnetic field values at all locations except those under the 66 kV line.

5. CONCLUSION

- The artificial staggering of line towers in case of parallel lines affect the magnetic field distribution beneath these lines. The degree of effect depends on the staggering distance.

- Reducing the line spacing between parallel lines of different voltage levels would reduce the maximum value of magnetic field in the two lines corridor. On the other hand, the maximum value of magnetic field under the lower voltage line increases and its location is shifted towards the higher voltage line.

- Reducing the loading of the higher voltage line for parallel lines of different voltage levels would reduce the magnetic field values at all locations. The maximum value of magnetic field is reduced by almost the same ratio.

- For the studied cases of phase arrangements for parallel lines of different voltage levels, the normal phase arrangement produces the lowest maximum magnetic field value while produces the highest magnetic field values at all locations except those under the higher voltage line.

6. REFERENCES

[1] Zemann, E., et al.: “Investigation of Exposition    to Low Frequency Magnetic Fields”, 9th International Symposium on High Voltage Engineering (ISH-95), Paper 8347, Graz, Austria, Aug./Sep. 1995.

[2] Abdallah, M. A, Mahmoud, Sh. A. and Anis, H. I.: “Interaction of Environmental ELF Electromagnetic Fields With Living Bodies”, Electric Machines and Power Systems,         28:301-312, 2000.

[3] Anis, H., Abd-allah, M. A. and Mahmoud, Sh. A.: “Comparative Exposure to Magnetic Fields Near High Voltage Transmission Lines”, 6th Middle East Power Systems Conference (MEPCON’98), Mansoura, Egypt, PP. 565-569, Dec. 1998.

[4] Tsanakas, D., et al. : “Compact and Optimum Phase Conductor Arrangement for the Reduction of Electric and Magnetic Fields of Overhead Lines”, Cigre, Paper 36-103, Paris,  2000.

[5] Isaka, K., et al. : “Characterization of Electric and Magnetic Fields at Ground Level Under EHV Transmission Lines”, 7th International Symposium on High Voltage Engineering  (ISH-91), Paper 93.01, Dresden, Germany,   Aug. 1991.

[6] Melo, M. O., et al.: “Electric and Magnetic Fields of Compact Transmission Lines”, IEEE Trans. on Power Delivery, Vol. 14, No. 1, PP. 200-204,    Jan. 1991.

[7] Mahmoud, Sh. A., Abd-allah, M. A. and Ahmed, Kh. G. : “Magnetic Fields Under Parallel Transmission Lines”, 8th Middle East Power Systems Conference (MEPCON’2001), Helwan,                                                                                                            Egypt, PP. 885-890, Dec. 2001.

[8] Anis, H., Abd-allah, M. A. and Mahmoud, Sh. A.: “Computation of Power Line Magnetic Fields - A Three Dimensional Approach”, 9th International Symposium on High Voltage Engineering (ISH-95), Paper 8333, Graz, Austria, Aug./Sep.  1995.

Address of Author

Dr. Shaher Anis Mahmoud

Egyptian Electricity Holding Company – 6th Floor

Abbassia, Nasr City, Cairo- Box 11517, Egypt

# Text boxes

Figure 1c: Line conductor configuration of 11 kV line

Figure 1b: Line conductor configuration of 66 kV line

Figure 1a: Line conductor configuration of 220 kV line

Figure 2: Lateral profiles at tower of parallel

220 kV lines

Figure 3: Lateral profiles at mid span of parallel

220 kV lines

Figure 6: Lateral profiles of parallel 220 kV

lines in case of artificial staggering

(Staggering distance = 90 m)

Figure 5: Lateral profiles of parallel 220 kV

lines in case of artificial staggering

(Staggering distance = 180 m)

Figure 4: Simulation of line tower staggering of   parallel lines

Figure 7: Vertical and horizontal projections of parallel 220 and 66 kV lines

Figure 9: Lateral profiles at mid span3 of 220 kV

line  for Parallel 220 and 66  kV lines

for different line spacings

Figure 8: Lateral profiles at tower of 220 kV line

for Parallel 220 and 66  kV lines

Figure 10: Lateral profiles at mid span3 of 220 kV

line for Parallel 220 and 66  kV lines

for different line loading

Figure 12: Lateral profiles at mid span3 of 66 kV

line  for Parallel 66 and 11  kV lines

for different phase arrangements

Figure 11: Lateral profiles at tower of 66 kV line

for Parallel 66 and 11 kV lines